## Test data
# Pressure-drop test data for Model 1110: one row per test point.
# Test data is assumed to be at standard air (0.075 lb/ft3). free_area_ft2 is optional.
# Rows starting with # are ignored. You can add your own columns to the right.
width_in | height_in | face_velocity_fpm | pressure_drop_in_wg | free_area_ft2
12 | 48 | 4006 | 0.368 | 2.877
12 | 48 | 3212 | 0.228 | 2.877
12 | 48 | 2412 | 0.124 | 2.877
12 | 48 | 1613 | 0.047 | 2.877
12 | 48 | 896 | 0.015 | 2.877
24 | 24 | 4357 | 0.261 | 3.012
24 | 24 | 3718 | 0.194 | 3.012
24 | 24 | 2731 | 0.111 | 3.012
24 | 24 | 1726 | 0.046 | 3.012
24 | 24 | 982 | 0.016 | 3.012
36 | 36 | 1400 | 0.015 | 7.217
36 | 36 | 2000 | 0.042 | 7.217
36 | 36 | 2500 | 0.07 | 7.217
36 | 36 | 3000 | 0.12 | 7.217
36 | 36 | 3500 | 0.18 | 7.217

## Free area
# Measured free areas (ft2), one row per size. Sizes listed here use this value directly.
width_in | height_in | free_area_ft2

## Blade table
# Blades per section by SECTION height (in). Each range includes both ends.
# Leave no gaps between rows (for example 10-14.99 and 15-20).
# Sections outside the table use blade_pitch_in from the Geometry sheet. Leave the table empty to always use the pitch.
min_height_in | max_height_in | blades
6 | 11 | 1
11.1 | 17 | 2
17.1 | 22 | 3
22.1 | 28 | 4
28.1 | 33 | 5
33.1 | 39 | 6
39.1 | 44 | 7
44.1 | 50 | 8
50.1 | 55 | 9
55.1 | 60 | 10
60.1 | 66 | 11
66.1 | 71 | 12
71.1 | 72 | 13

## Size rules
# Size limits and multi-section rules. Leave a value blank for no limit.
setting | value | notes
min_width_in | 6 | Smallest damper width made (in). Blank = no limit.
min_height_in | 6 | Smallest damper height made (in). Blank = no limit.
max_width_in | 500 | Largest overall width made (in). Blank = no limit.
max_height_in | 500 | Largest overall height made (in). Blank = no limit.
max_section_width_in | 48 | Largest single-section width (in). Wider dampers are split into equal sections. Blank = never split across the width.
max_section_height_in | 72 | Largest single-section height (in). Taller dampers are split into equal sections. Blank = never split up the height.
joint_blockage_in | 0.125 | Extra width blocked along each joint between sections (mullion, angles), beyond the section frames (in). 0 = none.

## Geometry
# Frame and blade dimensions used to estimate free area for sizes not in the Free area sheet.
setting | value | notes
description |  | Short description shown next to the model list (optional).
frame_obstruction_width_in | 1 | Frame/sleeve obstruction on EACH side, left and right (in).
frame_obstruction_height_in | 1.5 | Frame/sleeve obstruction on EACH side, top and bottom (in).
blade_thickness_in | 0.572 | Blade thickness facing the airflow when fully open (in).
blade_pitch_in | 5.5 | Blade spacing (in). Only used for section heights not in the Blade table.
other_blockage_in2 | 0 | Other blockage per section: linkage, jackshaft, stops (in2).