## Test data
# Pressure-drop test data for SAMPLE-FSD-200: one row per test point.
# Test data is assumed to be at standard air (0.075 lb/ft3). free_area_ft2 is optional.
# Rows starting with # are ignored. You can add your own columns to the right.
width_in | height_in | face_velocity_fpm | pressure_drop_in_wg | free_area_ft2
12 | 12 | 500 | 0.01
12 | 12 | 1000 | 0.06
12 | 12 | 1500 | 0.13
12 | 12 | 2000 | 0.23
12 | 12 | 2500 | 0.37
12 | 12 | 3000 | 0.53
24 | 24 | 500 | 0.01
24 | 24 | 1000 | 0.02
24 | 24 | 1500 | 0.06
24 | 24 | 2000 | 0.1
24 | 24 | 2500 | 0.16
24 | 24 | 3000 | 0.23
36 | 36 | 500 | 0.01
36 | 36 | 1000 | 0.02
36 | 36 | 1500 | 0.05
36 | 36 | 2000 | 0.09
36 | 36 | 2500 | 0.14
36 | 36 | 3000 | 0.21
48 | 12 | 500 | 0.01
48 | 12 | 1000 | 0.04
48 | 12 | 1500 | 0.1
48 | 12 | 2000 | 0.18
48 | 12 | 2500 | 0.29
48 | 12 | 3000 | 0.42
12 | 48 | 500 | 0.01
12 | 48 | 1000 | 0.03
12 | 48 | 1500 | 0.06
12 | 48 | 2000 | 0.11
12 | 48 | 2500 | 0.18
12 | 48 | 3000 | 0.25

## Free area
# Measured free areas (ft2), one row per size. Sizes listed here use this value directly.
width_in | height_in | free_area_ft2
8 | 8 | 0.21
12 | 12 | 0.62
16 | 16 | 1.23
24 | 12 | 1.39
24 | 24 | 3.11
30 | 30 | 5.06
36 | 36 | 7.48
48 | 48 | 13.72

## Blade table
# Blades per section by SECTION height (in). Each range includes both ends.
# Leave no gaps between rows (for example 10-14.99 and 15-20).
# Sections outside the table use blade_pitch_in from the Geometry sheet. Leave the table empty to always use the pitch.
min_height_in | max_height_in | blades

## Size rules
# Size limits and multi-section rules. Leave a value blank for no limit.
setting | value | notes
min_width_in | 8 | Smallest damper width made (in). Blank = no limit.
min_height_in | 8 | Smallest damper height made (in). Blank = no limit.
max_width_in | 180 | Largest overall width made (in). Blank = no limit.
max_height_in | 120 | Largest overall height made (in). Blank = no limit.
max_section_width_in | 60 | Largest single-section width (in). Wider dampers are split into equal sections. Blank = never split across the width.
max_section_height_in | 60 | Largest single-section height (in). Taller dampers are split into equal sections. Blank = never split up the height.
joint_blockage_in | 0 | Extra width blocked along each joint between sections (mullion, angles), beyond the section frames (in). 0 = none.

## Geometry
# Frame and blade dimensions used to estimate free area for sizes not in the Free area sheet.
setting | value | notes
description | SAMPLE - airfoil blades, low-profile frame (made-up data) | Short description shown next to the model list (optional).
frame_obstruction_width_in | 1 | Frame/sleeve obstruction on EACH side, left and right (in).
frame_obstruction_height_in | 1 | Frame/sleeve obstruction on EACH side, top and bottom (in).
blade_thickness_in | 0.75 | Blade thickness facing the airflow when fully open (in).
blade_pitch_in | 5 | Blade spacing (in). Only used for section heights not in the Blade table.
other_blockage_in2 | 0 | Other blockage per section: linkage, jackshaft, stops (in2).